## Secure
Datetime | Secure
2022-03-09 17:30:00 | TRUE
2022-03-09 17:45:00 | TRUE
2022-03-09 18:00:00 | TRUE

## Voltage Violations
vm_pu | va_degree | p_mw | q_mvar | Bus name | Datetime

## Overloaded Lines
line_name | line_loading_percent | Datetime

## Overloaded Transformers
trafo_name | trafo_loading_percent | Datetime

## Line Loadings
from_bus | to_bus | from_bus_name | to_bus_name | loading_percent | Datetime
0 | 2 | Hasle A | Snorrebakken | 9.089 | 2022-03-09 17:30:00
2 | 19 | Snorrebakken | Vaerket A | 6.7068 | 2022-03-09 17:30:00
21 | 19 | Vesthavnen | Vaerket A | 8.2121 | 2022-03-09 17:30:00
22 | 19 | Auxiliary bus Viadukten 1 | Vaerket A | 7.4611 | 2022-03-09 17:30:00
19 | 18 | Vaerket A | Ronne Syd | 4.1006 | 2022-03-09 17:30:00
4 | 21 | Ronne Nord | Vesthavnen | 7.4258 | 2022-03-09 17:30:00
0 | 4 | Hasle A | Ronne Nord | 17.5099 | 2022-03-09 17:30:00
23 | 4 | Auxiliary bus Viadukten 2 | Ronne Nord | 10.8277 | 2022-03-09 17:30:00
24 | 18 | Auxiliary bus Viadukten 3 | Ronne Syd | 4.6831 | 2022-03-09 17:30:00
11 | 18 | Aakirkeby | Ronne Syd | 5.2165 | 2022-03-09 17:30:00
11 | 9 | Aakirkeby | Bodilsker | 5.0221 | 2022-03-09 17:30:00
10 | 9 | Poulsker | Bodilsker | 2.9103 | 2022-03-09 17:30:00
8 | 9 | Nexo | Bodilsker | 7.6167 | 2022-03-09 17:30:00
12 | 9 | Dalslunde | Bodilsker | 2.745 | 2022-03-09 17:30:00
8 | 7 | Nexo | Svaneke | 4.4445 | 2022-03-09 17:30:00
12 | 7 | Dalslunde | Svaneke | 4.1226 | 2022-03-09 17:30:00
12 | 13 | Dalslunde | Osterlars | 0.48644 | 2022-03-09 17:30:00
15 | 13 | Gudhjem | Osterlars | 3.2339 | 2022-03-09 17:30:00
14 | 13 | Olsker | Osterlars | 3.0339 | 2022-03-09 17:30:00
14 | 6 | Olsker | Allinge | 2.2926 | 2022-03-09 17:30:00
14 | 0 | Olsker | Hasle A | 4.9998 | 2022-03-09 17:30:00
5 | 0 | BOR-HAS split 3 | Hasle A | 13.3349 | 2022-03-09 17:30:00
26 | 25 | BOR HAS split 2 | BOR HAS split 1 | 4.3012 | 2022-03-09 17:30:00
25 | 27 | BOR HAS split 1 | Borrby | 5.3937 | 2022-03-09 17:30:00
5 | 26 | BOR-HAS split 3 | BOR HAS split 2 | 12.8929 | 2022-03-09 17:30:00
0 | 2 | Hasle A | Snorrebakken | 9.3769 | 2022-03-09 17:45:00
2 | 19 | Snorrebakken | Vaerket A | 7.0952 | 2022-03-09 17:45:00
21 | 19 | Vesthavnen | Vaerket A | 8.5174 | 2022-03-09 17:45:00
22 | 19 | Auxiliary bus Viadukten 1 | Vaerket A | 7.8314 | 2022-03-09 17:45:00
19 | 18 | Vaerket A | Ronne Syd | 4.2963 | 2022-03-09 17:45:00
4 | 21 | Ronne Nord | Vesthavnen | 7.6878 | 2022-03-09 17:45:00
0 | 4 | Hasle A | Ronne Nord | 17.9676 | 2022-03-09 17:45:00
23 | 4 | Auxiliary bus Viadukten 2 | Ronne Nord | 11.1372 | 2022-03-09 17:45:00
24 | 18 | Auxiliary bus Viadukten 3 | Ronne Syd | 4.7032 | 2022-03-09 17:45:00
11 | 18 | Aakirkeby | Ronne Syd | 5.2337 | 2022-03-09 17:45:00
11 | 9 | Aakirkeby | Bodilsker | 5.0488 | 2022-03-09 17:45:00
10 | 9 | Poulsker | Bodilsker | 2.9029 | 2022-03-09 17:45:00
8 | 9 | Nexo | Bodilsker | 7.6444 | 2022-03-09 17:45:00
12 | 9 | Dalslunde | Bodilsker | 2.7695 | 2022-03-09 17:45:00
8 | 7 | Nexo | Svaneke | 4.4625 | 2022-03-09 17:45:00
12 | 7 | Dalslunde | Svaneke | 4.0929 | 2022-03-09 17:45:00
12 | 13 | Dalslunde | Osterlars | 0.39566 | 2022-03-09 17:45:00
15 | 13 | Gudhjem | Osterlars | 3.2315 | 2022-03-09 17:45:00
14 | 13 | Olsker | Osterlars | 2.961 | 2022-03-09 17:45:00
14 | 6 | Olsker | Allinge | 2.2923 | 2022-03-09 17:45:00
14 | 0 | Olsker | Hasle A | 4.9001 | 2022-03-09 17:45:00
5 | 0 | BOR-HAS split 3 | Hasle A | 13.4635 | 2022-03-09 17:45:00
26 | 25 | BOR HAS split 2 | BOR HAS split 1 | 2.8498 | 2022-03-09 17:45:00
25 | 27 | BOR HAS split 1 | Borrby | 3.5901 | 2022-03-09 17:45:00
5 | 26 | BOR-HAS split 3 | BOR HAS split 2 | 13.0064 | 2022-03-09 17:45:00
0 | 2 | Hasle A | Snorrebakken | 9.4815 | 2022-03-09 18:00:00
2 | 19 | Snorrebakken | Vaerket A | 7.2472 | 2022-03-09 18:00:00
21 | 19 | Vesthavnen | Vaerket A | 8.6151 | 2022-03-09 18:00:00
22 | 19 | Auxiliary bus Viadukten 1 | Vaerket A | 7.9403 | 2022-03-09 18:00:00
19 | 18 | Vaerket A | Ronne Syd | 4.3325 | 2022-03-09 18:00:00
4 | 21 | Ronne Nord | Vesthavnen | 7.7772 | 2022-03-09 18:00:00
0 | 4 | Hasle A | Ronne Nord | 18.1408 | 2022-03-09 18:00:00
23 | 4 | Auxiliary bus Viadukten 2 | Ronne Nord | 11.2466 | 2022-03-09 18:00:00
24 | 18 | Auxiliary bus Viadukten 3 | Ronne Syd | 4.6975 | 2022-03-09 18:00:00
11 | 18 | Aakirkeby | Ronne Syd | 5.2194 | 2022-03-09 18:00:00
11 | 9 | Aakirkeby | Bodilsker | 5.0439 | 2022-03-09 18:00:00
10 | 9 | Poulsker | Bodilsker | 2.8925 | 2022-03-09 18:00:00
8 | 9 | Nexo | Bodilsker | 7.6547 | 2022-03-09 18:00:00
12 | 9 | Dalslunde | Bodilsker | 2.7794 | 2022-03-09 18:00:00
8 | 7 | Nexo | Svaneke | 4.4689 | 2022-03-09 18:00:00
12 | 7 | Dalslunde | Svaneke | 4.0856 | 2022-03-09 18:00:00
12 | 13 | Dalslunde | Osterlars | 0.36744 | 2022-03-09 18:00:00
15 | 13 | Gudhjem | Osterlars | 3.227 | 2022-03-09 18:00:00
14 | 13 | Olsker | Osterlars | 2.9259 | 2022-03-09 18:00:00
14 | 6 | Olsker | Allinge | 2.2703 | 2022-03-09 18:00:00
14 | 0 | Olsker | Hasle A | 4.8244 | 2022-03-09 18:00:00
5 | 0 | BOR-HAS split 3 | Hasle A | 13.5436 | 2022-03-09 18:00:00
26 | 25 | BOR HAS split 2 | BOR HAS split 1 | 2.3881 | 2022-03-09 18:00:00
25 | 27 | BOR HAS split 1 | Borrby | 2.9725 | 2022-03-09 18:00:00
5 | 26 | BOR-HAS split 3 | BOR HAS split 2 | 13.0829 | 2022-03-09 18:00:00

## Transformer Loadings
name | loading_percent | Datetime
Borrby | 5.781 | 2022-03-09 17:30:00
Trf blok 6 |  | 2022-03-09 17:30:00
Trf blok 5 |  | 2022-03-09 17:30:00
Trf Vaerket 1 |  | 2022-03-09 17:30:00
Trf Vaerket 1 - 1 |  | 2022-03-09 17:30:00
Værket Trf 2 | 37.0941 | 2022-03-09 17:30:00
Snorrebakken Trf | 37.2504 | 2022-03-09 17:30:00
Hasle Trf 1 | 0 | 2022-03-09 17:30:00
Hasle Trf 2 | 8.5001 | 2022-03-09 17:30:00
Olsker Trf 1 | 6.513 | 2022-03-09 17:30:00
Olsker Trf 2 | 0 | 2022-03-09 17:30:00
Østerlars Trf 1 | 2.2176 | 2022-03-09 17:30:00
Aakirkeby Trf 22 | 0.1309 | 2022-03-09 17:30:00
Nexø Trf 1 | 4.6051 | 2022-03-09 17:30:00
Nexø Trf 2 | 0 | 2022-03-09 17:30:00
Bodilsker Trf 1 | 18.2983 | 2022-03-09 17:30:00
Rønne Syd Trf 1 | 42.586 | 2022-03-09 17:30:00
Allinge Trf 1 | 4.3749 | 2022-03-09 17:30:00
Allinge Trf 2 | 0 | 2022-03-09 17:30:00
Svaneke Trf 1 | 4.3244 | 2022-03-09 17:30:00
Viadukten Trf 1 | 6.4625 | 2022-03-09 17:30:00
Rønne Nord Trf 1 | 9.5015 | 2022-03-09 17:30:00
Poulsker Trf 1 | 3.3544 | 2022-03-09 17:30:00
Vesthavnen Trf 1 | 4.7601 | 2022-03-09 17:30:00
Gudhjem Trf 1 | 6.1392 | 2022-03-09 17:30:00
Borrby | 3.8479 | 2022-03-09 17:45:00
Trf blok 6 |  | 2022-03-09 17:45:00
Trf blok 5 |  | 2022-03-09 17:45:00
Trf Vaerket 1 |  | 2022-03-09 17:45:00
Trf Vaerket 1 - 1 |  | 2022-03-09 17:45:00
Værket Trf 2 | 38.8648 | 2022-03-09 17:45:00
Snorrebakken Trf | 38.0722 | 2022-03-09 17:45:00
Hasle Trf 1 | 0 | 2022-03-09 17:45:00
Hasle Trf 2 | 8.0969 | 2022-03-09 17:45:00
Olsker Trf 1 | 6.1305 | 2022-03-09 17:45:00
Olsker Trf 2 | 0 | 2022-03-09 17:45:00
Østerlars Trf 1 | 2.2195 | 2022-03-09 17:45:00
Aakirkeby Trf 22 | 0.10157 | 2022-03-09 17:45:00
Nexø Trf 1 | 4.5287 | 2022-03-09 17:45:00
Nexø Trf 2 | 0 | 2022-03-09 17:45:00
Bodilsker Trf 1 | 18.3128 | 2022-03-09 17:45:00
Rønne Syd Trf 1 | 42.6064 | 2022-03-09 17:45:00
Allinge Trf 1 | 4.3654 | 2022-03-09 17:45:00
Allinge Trf 2 | 0 | 2022-03-09 17:45:00
Svaneke Trf 1 | 4.2492 | 2022-03-09 17:45:00
Viadukten Trf 1 | 6.2335 | 2022-03-09 17:45:00
Rønne Nord Trf 1 | 9.3912 | 2022-03-09 17:45:00
Poulsker Trf 1 | 3.2487 | 2022-03-09 17:45:00
Vesthavnen Trf 1 | 4.6906 | 2022-03-09 17:45:00
Gudhjem Trf 1 | 5.9562 | 2022-03-09 17:45:00
Borrby | 3.186 | 2022-03-09 18:00:00
Trf blok 6 |  | 2022-03-09 18:00:00
Trf blok 5 |  | 2022-03-09 18:00:00
Trf Vaerket 1 |  | 2022-03-09 18:00:00
Trf Vaerket 1 - 1 |  | 2022-03-09 18:00:00
Værket Trf 2 | 39.4118 | 2022-03-09 18:00:00
Snorrebakken Trf | 38.3595 | 2022-03-09 18:00:00
Hasle Trf 1 | 0 | 2022-03-09 18:00:00
Hasle Trf 2 | 7.9883 | 2022-03-09 18:00:00
Olsker Trf 1 | 5.7058 | 2022-03-09 18:00:00
Olsker Trf 2 | 0 | 2022-03-09 18:00:00
Østerlars Trf 1 | 2.1841 | 2022-03-09 18:00:00
Aakirkeby Trf 22 | 0.091725 | 2022-03-09 18:00:00
Nexø Trf 1 | 4.443 | 2022-03-09 18:00:00
Nexø Trf 2 | 0 | 2022-03-09 18:00:00
Bodilsker Trf 1 | 18.32 | 2022-03-09 18:00:00
Rønne Syd Trf 1 | 42.6181 | 2022-03-09 18:00:00
Allinge Trf 1 | 4.2131 | 2022-03-09 18:00:00
Allinge Trf 2 | 0 | 2022-03-09 18:00:00
Svaneke Trf 1 | 4.3108 | 2022-03-09 18:00:00
Viadukten Trf 1 | 6.1487 | 2022-03-09 18:00:00
Rønne Nord Trf 1 | 9.1228 | 2022-03-09 18:00:00
Poulsker Trf 1 | 3.1181 | 2022-03-09 18:00:00
Vesthavnen Trf 1 | 4.6402 | 2022-03-09 18:00:00
Gudhjem Trf 1 | 5.7335 | 2022-03-09 18:00:00

## Bus Voltages Injections
vm_pu | va_degree | p_mw | q_mvar | Bus name | Datetime
0.98841 | -0.22231 | 0 | 0 | Hasle A | 2022-03-09 17:30:00
|  | 0 | 0 | Hasle B | 2022-03-09 17:30:00
0.986 | -0.11509 | 0 | 0 | Snorrebakken | 2022-03-09 17:30:00
|  | 0 | 0 | Olsker | 2022-03-09 17:30:00
0.98636 | -0.12502 | 0 | 0 | Ronne Nord | 2022-03-09 17:30:00
0.98883 | -0.23456 | 0 | 0 | BOR-HAS split 3 | 2022-03-09 17:30:00
0.98904 | -0.3502 | 0 | 0 | Allinge | 2022-03-09 17:30:00
0.98997 | -0.51473 | 0 | 0 | Svaneke | 2022-03-09 17:30:00
0.98965 | -0.49291 | 0 | 0 | Nexo | 2022-03-09 17:30:00
0.98951 | -0.45727 | 0 | 0 | Bodilsker | 2022-03-09 17:30:00
0.9895 | -0.47065 | 0 | 0 | Poulsker | 2022-03-09 17:30:00
0.98775 | -0.28537 | 0 | 0 | Aakirkeby | 2022-03-09 17:30:00
0.98999 | -0.48848 | 0 | 0 | Dalslunde | 2022-03-09 17:30:00
0.99003 | -0.47277 | 0 | 0 | Osterlars | 2022-03-09 17:30:00
0.98909 | -0.34171 | 0 | 0 | Olsker | 2022-03-09 17:30:00
0.99007 | -0.48839 | 0 | 0 | Gudhjem | 2022-03-09 17:30:00
0.98605 | -0.10808 | 0 | 0 | Viadukten A | 2022-03-09 17:30:00
|  | 0 | 0 | Viadukten B | 2022-03-09 17:30:00
0.98589 | -0.10513 | 0 | 0 | Ronne Syd | 2022-03-09 17:30:00
0.98593 | -0.095969 | 0 | 0 | Vaerket A | 2022-03-09 17:30:00
|  | 0 | 0 | Vaerket B | 2022-03-09 17:30:00
0.98612 | -0.11056 | 0 | 0 | Vesthavnen | 2022-03-09 17:30:00
0.98605 | -0.10808 | 0 | 0 | Auxiliary bus Viadukten 1 | 2022-03-09 17:30:00
0.98605 | -0.10808 | 0 | 0 | Auxiliary bus Viadukten 2 | 2022-03-09 17:30:00
0.98605 | -0.10808 | 0 | 0 | Auxiliary bus Viadukten 3 | 2022-03-09 17:30:00
0.99841 | -0.41924 | 0 | 0 | BOR HAS split 1 | 2022-03-09 17:30:00
0.99836 | -0.42256 | 0 | 0 | BOR HAS split 2 | 2022-03-09 17:30:00
0.99863 | -0.345 | 0 | 0 | Borrby | 2022-03-09 17:30:00
0.91 | 0 | -3.111 | 1.1302 | Tomelilla | 2022-03-09 17:30:00
|  | 0 | 0 | Vaerket Blok 6 | 2022-03-09 17:30:00
|  | 0 | 0 | Vaerket Blok 5 | 2022-03-09 17:30:00
|  | 0 | 0 | Vaerket Diesler | 2022-03-09 17:30:00
|  | 0 | 0 | Vaer N | 2022-03-09 17:30:00
1 | 0.53899 | 0 | 4 | Dampværk A | 2022-03-09 17:30:00
1 | 0.53899 | 0 | 0 | Dampværk B | 2022-03-09 17:30:00
1 | 0.53899 | 0 | 0 | Aux bus trafo DMP | 2022-03-09 17:30:00
1 | 0.53899 | -3.2858 | 6.5124 | Aux bus trafo DMP 2 | 2022-03-09 17:30:00
1 | -0.13723 | 0.30032 | 3.4967 | Snorrebakken 10 kV | 2022-03-09 17:30:00
0.98841 | -0.22231 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 17:30:00
0.98841 | -0.22231 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 17:30:00
1.0347 | -0.657 | 0.83796 | 0 | Hasle 10 kV | 2022-03-09 17:30:00
0.98872 | -0.60609 | 0.26955 | 0 | Olsker 10 kV | 2022-03-09 17:30:00
1.0369 | -0.58235 | 0.34225 | 0 | Østerlars 10 kV | 2022-03-09 17:30:00
1.0347 | -0.28964 | 0.01388 | 0 | Åkirkeby 10 kV | 2022-03-09 17:30:00
1.0366 | -0.70895 | 0.45567 | 0 | Nexø 10 kV | 2022-03-09 17:30:00
1.0199 | -0.40335 | 0.00577 | 2.0803 | Bodilsker 10 kV | 2022-03-09 17:30:00
0.99607 | -0.22022 | 0.52649 | 3.9687 | Rønne Syd 10 kV | 2022-03-09 17:30:00
1.0356 | -0.56027 | 0.42962 | 0 | Allinge 10 kV | 2022-03-09 17:30:00
1.0366 | -0.71987 | 0.42501 | 0 | Svaneke 10 kV | 2022-03-09 17:30:00
1.0324 | -0.40238 | 0.63489 | 0 | Viadukten 10 kV | 2022-03-09 17:30:00
0.98605 | -0.10808 | 0 | 0 | Auxiliary bus Viadukten 4 | 2022-03-09 17:30:00
1.0325 | -0.56062 | 0.93501 | 0 | Rønne Nord 10 kV | 2022-03-09 17:30:00
1.0362 | -0.62575 | 0.32809 | 0 | Poulsker 10 kV | 2022-03-09 17:30:00
1.0326 | -0.33209 | 0.46657 | 0 | Vesthavnen 10 kV | 2022-03-09 17:30:00
0.98971 | -0.73047 | 0.25423 | 0 | Gudhjem 10 kV | 2022-03-09 17:30:00
0.98905 | 0.02537 | 0 | 0 | Hasle A | 2022-03-09 17:45:00
|  | 0 | 0 | Hasle B | 2022-03-09 17:45:00
0.9867 | 0.14553 | 0 | 0 | Snorrebakken | 2022-03-09 17:45:00
|  | 0 | 0 | Olsker | 2022-03-09 17:45:00
0.9871 | 0.13519 | 0 | 0 | Ronne Nord | 2022-03-09 17:45:00
0.98945 | 0.010198 | 0 | 0 | BOR-HAS split 3 | 2022-03-09 17:45:00
0.98971 | -0.099025 | 0 | 0 | Allinge | 2022-03-09 17:45:00
0.99073 | -0.25426 | 0 | 0 | Svaneke | 2022-03-09 17:45:00
0.99042 | -0.23203 | 0 | 0 | Nexo | 2022-03-09 17:45:00
0.99028 | -0.19628 | 0 | 0 | Bodilsker | 2022-03-09 17:45:00
0.99027 | -0.20952 | 0 | 0 | Poulsker | 2022-03-09 17:45:00
0.98851 | -0.023352 | 0 | 0 | Aakirkeby | 2022-03-09 17:45:00
0.99075 | -0.22843 | 0 | 0 | Dalslunde | 2022-03-09 17:45:00
0.99076 | -0.2163 | 0 | 0 | Osterlars | 2022-03-09 17:45:00
0.98977 | -0.090551 | 0 | 0 | Olsker | 2022-03-09 17:45:00
0.9908 | -0.23181 | 0 | 0 | Gudhjem | 2022-03-09 17:45:00
0.98679 | 0.15384 | 0 | 0 | Viadukten A | 2022-03-09 17:45:00
|  | 0 | 0 | Viadukten B | 2022-03-09 17:45:00
0.98664 | 0.15712 | 0 | 0 | Ronne Syd | 2022-03-09 17:45:00
0.98668 | 0.1669 | 0 | 0 | Vaerket A | 2022-03-09 17:45:00
|  | 0 | 0 | Vaerket B | 2022-03-09 17:45:00
0.98687 | 0.15113 | 0 | 0 | Vesthavnen | 2022-03-09 17:45:00
0.98679 | 0.15384 | 0 | 0 | Auxiliary bus Viadukten 1 | 2022-03-09 17:45:00
0.98679 | 0.15384 | 0 | 0 | Auxiliary bus Viadukten 2 | 2022-03-09 17:45:00
0.98679 | 0.15384 | 0 | 0 | Auxiliary bus Viadukten 3 | 2022-03-09 17:45:00
0.99782 | -0.27671 | 0 | 0 | BOR HAS split 1 | 2022-03-09 17:45:00
0.99778 | -0.27859 | 0 | 0 | BOR HAS split 2 | 2022-03-09 17:45:00
0.99802 | -0.22875 | 0 | 0 | Borrby | 2022-03-09 17:45:00
0.91 | 0 | -2.0654 | 0.7598 | Tomelilla | 2022-03-09 17:45:00
|  | 0 | 0 | Vaerket Blok 6 | 2022-03-09 17:45:00
|  | 0 | 0 | Vaerket Blok 5 | 2022-03-09 17:45:00
|  | 0 | 0 | Vaerket Diesler | 2022-03-09 17:45:00
|  | 0 | 0 | Vaer N | 2022-03-09 17:45:00
1 | 0.95115 | 0 | 4 | Dampværk A | 2022-03-09 17:45:00
1 | 0.95115 | 0 | 0 | Dampværk B | 2022-03-09 17:45:00
1 | 0.95115 | 0 | 0 | Aux bus trafo DMP | 2022-03-09 17:45:00
1 | 0.95115 | -4.1385 | 6.7823 | Aux bus trafo DMP 2 | 2022-03-09 17:45:00
1 | 0.14042 | 0.27326 | 3.5776 | Snorrebakken 10 kV | 2022-03-09 17:45:00
0.98905 | 0.02537 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 17:45:00
0.98905 | 0.02537 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 17:45:00
1.0354 | -0.38832 | 0.79861 | 0 | Hasle 10 kV | 2022-03-09 17:45:00
0.9894 | -0.3391 | 0.25379 | 0 | Olsker 10 kV | 2022-03-09 17:45:00
1.0376 | -0.3259 | 0.3428 | 0 | Østerlars 10 kV | 2022-03-09 17:45:00
1.0355 | -0.024748 | 0.00165 | 0 | Åkirkeby 10 kV | 2022-03-09 17:45:00
1.0374 | -0.44433 | 0.44846 | 0 | Nexø 10 kV | 2022-03-09 17:45:00
1.0207 | -0.13451 | -0.01213 | 2.0836 | Bodilsker 10 kV | 2022-03-09 17:45:00
0.99684 | 0.046553 | 0.51832 | 3.9747 | Rønne Syd 10 kV | 2022-03-09 17:45:00
1.0363 | -0.30849 | 0.42897 | 0 | Allinge 10 kV | 2022-03-09 17:45:00
1.0374 | -0.45561 | 0.41784 | 0 | Svaneke 10 kV | 2022-03-09 17:45:00
1.0332 | -0.12972 | 0.61273 | 0 | Viadukten 10 kV | 2022-03-09 17:45:00
0.98679 | 0.15384 | 0 | 0 | Auxiliary bus Viadukten 4 | 2022-03-09 17:45:00
1.0333 | -0.29501 | 0.92482 | 0 | Rønne Nord 10 kV | 2022-03-09 17:45:00
1.037 | -0.35947 | 0.31776 | 0 | Poulsker 10 kV | 2022-03-09 17:45:00
1.0334 | -0.066955 | 0.46003 | 0 | Vesthavnen 10 kV | 2022-03-09 17:45:00
0.99044 | -0.46644 | 0.24678 | 0 | Gudhjem 10 kV | 2022-03-09 17:45:00
0.98928 | 0.11015 | 0 | 0 | Hasle A | 2022-03-09 18:00:00
|  | 0 | 0 | Hasle B | 2022-03-09 18:00:00
0.98695 | 0.23427 | 0 | 0 | Snorrebakken | 2022-03-09 18:00:00
|  | 0 | 0 | Olsker | 2022-03-09 18:00:00
0.98735 | 0.22392 | 0 | 0 | Ronne Nord | 2022-03-09 18:00:00
0.98967 | 0.093984 | 0 | 0 | BOR-HAS split 3 | 2022-03-09 18:00:00
0.98998 | -0.01132 | 0 | 0 | Allinge | 2022-03-09 18:00:00
0.99103 | -0.16266 | 0 | 0 | Svaneke | 2022-03-09 18:00:00
0.99072 | -0.14018 | 0 | 0 | Nexo | 2022-03-09 18:00:00
0.99058 | -0.10438 | 0 | 0 | Bodilsker | 2022-03-09 18:00:00
0.99058 | -0.11745 | 0 | 0 | Poulsker | 2022-03-09 18:00:00
0.9888 | 0.0677 | 0 | 0 | Aakirkeby | 2022-03-09 18:00:00
0.99105 | -0.13693 | 0 | 0 | Dalslunde | 2022-03-09 18:00:00
0.99105 | -0.12598 | 0 | 0 | Osterlars | 2022-03-09 18:00:00
0.99003 | -0.002985 | 0 | 0 | Olsker | 2022-03-09 18:00:00
0.99109 | -0.14136 | 0 | 0 | Gudhjem | 2022-03-09 18:00:00
0.98705 | 0.24308 | 0 | 0 | Viadukten A | 2022-03-09 18:00:00
|  | 0 | 0 | Viadukten B | 2022-03-09 18:00:00
0.9869 | 0.24648 | 0 | 0 | Ronne Syd | 2022-03-09 18:00:00
0.98694 | 0.25638 | 0 | 0 | Vaerket A | 2022-03-09 18:00:00
|  | 0 | 0 | Vaerket B | 2022-03-09 18:00:00
0.98713 | 0.24028 | 0 | 0 | Vesthavnen | 2022-03-09 18:00:00
0.98705 | 0.24308 | 0 | 0 | Auxiliary bus Viadukten 1 | 2022-03-09 18:00:00
0.98705 | 0.24308 | 0 | 0 | Auxiliary bus Viadukten 2 | 2022-03-09 18:00:00
0.98705 | 0.24308 | 0 | 0 | Auxiliary bus Viadukten 3 | 2022-03-09 18:00:00
0.99763 | -0.22777 | 0 | 0 | BOR HAS split 1 | 2022-03-09 18:00:00
0.99759 | -0.22915 | 0 | 0 | BOR HAS split 2 | 2022-03-09 18:00:00
0.99781 | -0.18882 | 0 | 0 | Borrby | 2022-03-09 18:00:00
0.91 | 0 | -1.7064 | 0.63425 | Tomelilla | 2022-03-09 18:00:00
|  | 0 | 0 | Vaerket Blok 6 | 2022-03-09 18:00:00
|  | 0 | 0 | Vaerket Blok 5 | 2022-03-09 18:00:00
|  | 0 | 0 | Vaerket Diesler | 2022-03-09 18:00:00
|  | 0 | 0 | Vaer N | 2022-03-09 18:00:00
1 | 1.079 | 0 | 4 | Dampværk A | 2022-03-09 18:00:00
1 | 1.079 | 0 | 0 | Dampværk B | 2022-03-09 18:00:00
1 | 1.079 | 0 | 0 | Aux bus trafo DMP | 2022-03-09 18:00:00
1 | 1.079 | -4.3574 | 6.8739 | Aux bus trafo DMP 2 | 2022-03-09 18:00:00
1 | 0.22957 | 0.27446 | 3.605 | Snorrebakken 10 kV | 2022-03-09 18:00:00
0.98928 | 0.11015 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 18:00:00
0.98928 | 0.11015 | 0 | 0 | Aux bus trafo HASLE | 2022-03-09 18:00:00
1.0357 | -0.29786 | 0.78804 | 0 | Hasle 10 kV | 2022-03-09 18:00:00
0.98968 | -0.2341 | 0.23614 | 0 | Olsker 10 kV | 2022-03-09 18:00:00
1.0379 | -0.2337 | 0.33713 | 0 | Østerlars 10 kV | 2022-03-09 18:00:00
1.0358 | 0.069276 | -0.01101 | 0 | Åkirkeby 10 kV | 2022-03-09 18:00:00
1.0377 | -0.34839 | 0.44011 | 0 | Nexø 10 kV | 2022-03-09 18:00:00
1.021 | -0.035149 | -0.02918 | 2.0849 | Bodilsker 10 kV | 2022-03-09 18:00:00
0.9971 | 0.13574 | 0.51894 | 3.9768 | Rønne Syd 10 kV | 2022-03-09 18:00:00
1.0366 | -0.21329 | 0.41392 | 0 | Allinge 10 kV | 2022-03-09 18:00:00
1.0378 | -0.36691 | 0.4241 | 0 | Svaneke 10 kV | 2022-03-09 18:00:00
1.0335 | -0.036518 | 0.6045 | 0 | Viadukten 10 kV | 2022-03-09 18:00:00
0.98705 | 0.24308 | 0 | 0 | Auxiliary bus Viadukten 4 | 2022-03-09 18:00:00
1.0336 | -0.19381 | 0.89856 | 0 | Rønne Nord 10 kV | 2022-03-09 18:00:00
1.0373 | -0.26116 | 0.30477 | 0 | Poulsker 10 kV | 2022-03-09 18:00:00
1.0337 | 0.024635 | 0.45515 | 0 | Vesthavnen 10 kV | 2022-03-09 18:00:00
0.99074 | -0.36706 | 0.23755 | 0 | Gudhjem 10 kV | 2022-03-09 18:00:00