## bus
| name | vn_kv | type | zone | in_service | description | substat | folder_id | equipment
0 | Hasle A | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
1 | Hasle B | 63 | b | Net 60kV | FALSE | Net 60kV |  | Net 60kV
2 | Værket A | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
3 | Værket B | 63 | b | Net 60kV | FALSE | Net 60kV |  | Net 60kV
4 | Værket C VIA | 63 | m | Net 60kV | TRUE | Net 60kV |  | Net 60kV
5 | Snorrebakken | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
6 | Olsker | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
7 | Allinge | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
8 | Østerlars | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
9 | Gudhjem | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
10 | Dalslunde | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
11 | Svaneke | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
12 | Bodilsker | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
13 | Poulsker | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
14 | Åkirkeby | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
15 | Rønne Syd | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
16 | Nexø | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
17 | Viadukten A | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
18 | Viadukten B | 63 | b | Net 60kV | FALSE | Net 60kV |  | Net 60kV
19 | Viadukten C VÆR | 63 | m | Net 60kV | TRUE | Net 60kV |  | Net 60kV
20 | Viadukten C SYD | 63 | m | Net 60kV | TRUE | Net 60kV |  | Net 60kV
21 | Viadukten C NOR | 63 | m | Net 60kV | TRUE | Net 60kV |  | Net 60kV
22 | Rønne Nord | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
23 | Vesthavnen | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
24 | Værket C VES | 63 | m | Net 60kV | TRUE | Net 60kV |  | Net 60kV
25 | Værket C Trf 1 Diesler | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
26 | Værket C SYD | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
27 | Hasle C OLS | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
28 | Hasle C NOR | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
29 | Hasle C BOR | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
30 | Værket C Trf 2 Gl. Dampværk | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
31 | Værket C block 5 | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
32 | Værket C SNO | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
33 | Hasle C SNO | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
34 | Værket C block 6 | 63 | b | Net 60kV | TRUE | Net 60kV |  | Net 60kV
35 | Viadukten AB Trf | 63 | m | 11 Viadukten | TRUE | 11 Viadukten |  | 11 Viadukten
36 | Viadukten 10kV | 10.5 | b | 11 Viadukten | TRUE | 11 Viadukten |  | 11 Viadukten
37 | Gl Dampværk B 10.5 kV | 10.5 | b | 00 Gl Dampværk | TRUE | 00 Gl Dampværk |  | 00 Gl Dampværk
38 | Gl Dampværk C Trf 2 | 10.5 | m | 00 Gl Dampværk | TRUE | 00 Gl Dampværk |  | 00 Gl Dampværk
39 | Gl Dampværket C afg Load | 10.5 | m | 00 Gl Dampværk | TRUE | 00 Gl Dampværk |  | 00 Gl Dampværk
40 | Gl Dampværk A 10.5 kV | 10.5 | b | 00 Gl Dampværk | TRUE | 00 Gl Dampværk |  | 00 Gl Dampværk
41 | Gl Dampværket afg Load Blok 7 | 10.5 | m | 00 Gl Dampværk | FALSE | 00 Gl Dampværk |  | 00 Gl Dampværk
42 | Rønne Nord 10 kV | 10.5 | b | 12 Rønne Nord | TRUE | 12 Rønne Nord |  | 12 Rønne Nord
43 | Nexø 10.5 kV | 10.5 | b | 06 Nexø | TRUE | 06 Nexø |  | 06 Nexø
44 | Bodilsker 10.5 kV | 10.5 | b | 07 Bodilsker | TRUE | 07 Bodilsker |  | 07 Bodilsker
45 | Poulsker 10.5 kV | 10.5 | b | 13 Povlsker | TRUE | 13 Povlsker |  | 13 Povlsker
46 | Åkirkeby 10.5 kV | 10.5 | b | 05 Åkirkeby | TRUE | 05 Åkirkeby |  | 05 Åkirkeby
47 | Snorrebakken 10 kV | 10.5 | b | 01 Snorrebakken | TRUE | 01 Snorrebakken |  | 01 Snorrebakken
48 | Vesthavnen 10 kV | 10.5 | b | 14 Vesthavnen | TRUE | 14 Vesthavnen |  | 14 Vesthavnen
49 | Hasle 10kV | 10.5 | b | 02 Hasle | TRUE | 02 Hasle |  | 02 Hasle
50 | Hasle C Trf2 | 63 | b | 02 Hasle | TRUE | 02 Hasle |  | 02 Hasle
51 | Hasle C Trf 1 | 63 | b | 02 Hasle | TRUE | 02 Hasle |  | 02 Hasle
52 | Hasle AB Trf test | 63 | b | 02 Hasle | FALSE | 02 Hasle |  | 02 Hasle
53 | HAS TRF1 HV | 60 | m | 02 Hasle | FALSE | 02 Hasle |  | 02 Hasle
54 | HAS TRF1 LV | 10 | m | 02 Hasle | FALSE | 02 Hasle |  | 02 Hasle
55 | Rønne Syd 10.5 kV | 10.5 | b | 08 Rønne Syd | TRUE | 08 Rønne Syd |  | 08 Rønne Syd
56 | Værket Diesler | 10.5 | b | Gen Værket | TRUE | Gen Værket |  | Gen Værket
57 | VÆR N | 63 | b | Gen Værket | FALSE | Gen Værket |  | Gen Værket
58 | Olsker 10 kV | 10.5 | b | 03 Olsker | TRUE | 03 Olsker |  | 03 Olsker
59 | Allinge 10 kV | 10.5 | b | 09 Allinge | TRUE | 09 Allinge |  | 09 Allinge
60 | Østerlars 10 kV | 10.5 | b | 04 Østerlars | TRUE | 04 Østerlars |  | 04 Østerlars
61 | Gudhjem 10 kV | 10.5 | b | 15 Gudhjem | TRUE | 15 Gudhjem |  | 15 Gudhjem
62 | Svaneke 10 kV | 10.5 | b | 10 Svaneke | TRUE | 10 Svaneke |  | 10 Svaneke
63 | Værket A_aux | 63 | n |  | FALSE
64 | Værket B_aux | 63 | n |  | FALSE
65 | Værket A_aux | 63 | n |  | FALSE
66 | Værket B_aux | 63 | n |  | FALSE
67 | Værket A_aux | 63 | n |  | FALSE
68 | Værket B_aux | 63 | n |  | FALSE
69 | Værket A_aux | 63 | n |  | FALSE
70 | Værket B_aux | 63 | n |  | FALSE
71 | HAS-OLS (Muff 1) | 63 | ls | Net 60kV | TRUE
72 | HAS-SNO (Muff 1) | 63 | ls | Net 60kV | TRUE
73 | SNO-VÆR (Muff 1) | 63 | ls | Net 60kV | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | description | equipment
0 | Blok 5 | 31 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
1 | Blok 6 | 34 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
2 | 11 VIA Load | 36 | 0.929 | 0.478 | 0 | 0 |  | 1 | TRUE | wye
3 | 00 Gl Dampværk Load | 39 | 1.37 | 0.26 | 0 | 0 |  | 1 | TRUE | wye
4 | 12 NOR Load | 42 | 0.866 | 0.58 | 0 | 0 |  | 1 | TRUE | wye
5 | 06 NEX Load | 43 | 1.079 | 0.137 | 0 | 0 |  | 1 | TRUE | wye
6 | 07 BOD Load | 44 | 0.618 | -0.026 | 0 | 0 |  | 1 | TRUE | wye
7 | 13 POU Load | 45 | 0.405 | -0.546 | 0 | 0 |  | 1 | TRUE | wye
8 | 05 ÅKI Load | 46 | 1.587 | -0.578 | 0 | 0 |  | 1 | TRUE | wye
9 | 01 SNO Load | 47 | 0.883 | 0.129 | 0 | 0 |  | 1 | TRUE | wye
10 | 14 VES Load | 48 | 0.317 | -0.154 | 0 | 0 |  | 1 | TRUE | wye
11 | 02 HAS Load | 49 | 0.641 | -0.437 | 0 | 0 |  | 1 | TRUE | wye
12 | 08 SYD Load | 55 | 1.128 | -0.214 | 0 | 0 |  | 1 | TRUE | wye
13 | Diesel generatorer | 56 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
14 | 03 OLS Load | 58 | 0.615 | -0.354 | 0 | 0 |  | 1 | TRUE | wye
15 | 09 ALL Load | 59 | 0.78 | -0.266 | 0 | 0 |  | 1 | TRUE | wye
16 | 04 ØST Load | 60 | 0.922 | -0.109 | 0 | 0 |  | 1 | TRUE | wye
17 | 15 GUD Load | 61 | 0.608 | -0.143 | 0 | 0 |  | 1 | TRUE | wye
18 | 10 SVA Load | 62 | 0.923 | 0.043 | 0 | 0 |  | 1 | TRUE | wye

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 36 | 0 | t | CB | TRUE | Viadukten 10kV\Cub_1\Switch | 0
1 | 22 | 1 | t | CB | TRUE | Rønne Nord\Cub_4\Switch | 0
2 | 42 | 1 | t | CB | TRUE | Rønne Nord 10 kV\Cub_1\Switch | 0
3 | 16 | 2 | t | CB | TRUE | Nexø\NEX TRF1 60kV\Switch | 0
4 | 43 | 2 | t | CB | TRUE | Nexø 10.5 kV\NEX TRF1 10kV\Switch | 0
5 | 16 | 3 | t | CB | FALSE | Nexø\NEX TRF2 60kV\Switch | 0
6 | 43 | 3 | t | CB | FALSE | Nexø 10.5 kV\NEX TRF2 10kV\Switch | 0
7 | 12 | 4 | t | CB | TRUE | Bodilsker\BOD TRF1 60kV\Switch | 0
8 | 44 | 4 | t | CB | TRUE | Bodilsker 10.5 kV\BOD TRF1 10kV\Switch | 0
9 | 13 | 5 | t | CB | TRUE | Poulsker\POV TRF1 60kV\Switch | 0
10 | 45 | 5 | t | CB | TRUE | Poulsker 10.5 kV\POV TRF1 10kV\Switch | 0
11 | 14 | 6 | t | CB | FALSE | Åkirkeby\Cub_4\Switch | 0
12 | 46 | 6 | t | CB | FALSE | Åkirkeby 10.5 kV\Cub_2\Switch | 0
13 | 14 | 7 | t | CB | TRUE | Åkirkeby\Cub_5\Switch | 0
14 | 46 | 7 | t | CB | TRUE | Åkirkeby 10.5 kV\Cub_22\Switch | 0
15 | 5 | 8 | t | CB | TRUE | Snorrebakken\SNO TRF1 60kV\Switch | 0
16 | 47 | 8 | t | CB | TRUE | Snorrebakken 10 kV\SNO TRF1 10kV\Switch | 0
17 | 23 | 9 | t | CB | TRUE | Vesthavnen\Cub_3\Switch | 0
18 | 48 | 9 | t | CB | TRUE | Vesthavnen 10 kV\Cub_1\Switch | 0
19 | 50 | 10 | t | CB | TRUE | Hasle C Trf2\Cub_1\Switch | 0
20 | 49 | 10 | t | CB | TRUE | Hasle 10kV\HAS TRF 2 10kV\Switch | 0
21 | 15 | 12 | t | CB | TRUE | Rønne Syd\Cub_9\Switch | 0
22 | 55 | 12 | t | CB | TRUE | Rønne Syd 10.5 kV\Cub_1\Switch | 0
23 | 25 | 13 | t | CB | TRUE | Værket C Trf 1 Diesler\Trf1 Diesler HV-side\Switch | 0
24 | 56 | 13 | t | CB | TRUE | Værket Diesler\Trf1 Diesler MV-side\Switch | 0
25 | 30 | 14 | t | CB | TRUE | Værket C Trf 2 Gl. Dampværk\Cub_1\Switch VÆR_ AB1-SNO | 0
26 | 6 | 15 | t | CB | TRUE | Olsker\OLS TRF1 60kV\Switch | 0
27 | 58 | 15 | t | CB | TRUE | Olsker 10 kV\OLS TRF1 10kV\Switch | 0
28 | 6 | 16 | t | CB | FALSE | Olsker\OLS TRF2 60kV\Switch | 0
29 | 58 | 16 | t | CB | FALSE | Olsker 10 kV\OLS TRF2 10kV\Switch | 0
30 | 7 | 17 | t | CB | TRUE | Allinge\Cub_2\Switch | 0
31 | 59 | 17 | t | CB | TRUE | Allinge 10 kV\Cub_1\Switch | 0
32 | 7 | 18 | t | CB | FALSE | Allinge\Cub_3\Switch | 0
33 | 59 | 18 | t | CB | FALSE | Allinge 10 kV\Cub_2\Switch | 0
34 | 8 | 19 | t | CB | TRUE | Østerlars\ØST TRF1 60kV\Switch | 0
35 | 60 | 19 | t | CB | TRUE | Østerlars 10 kV\ØST TRF1 10kV\Switch | 0
36 | 9 | 20 | t | CB | TRUE | Gudhjem\Cub_2\Switch | 0
37 | 61 | 20 | t | CB | TRUE | Gudhjem 10 kV\Cub_1\Switch | 0
38 | 11 | 21 | t | CB | TRUE | Svaneke\SVA TRF1 60kV\Switch | 0
39 | 62 | 21 | t | CB | TRUE | Svaneke 10 kV\SVA TRF1 10kV\Switch | 0
40 | 0 | 33 | b | CB | TRUE | Hasle A HAS-SNO | 0
41 | 1 | 33 | b | CB | FALSE | Hasle B1 | 0
42 | 0 | 27 | b | CB | TRUE | Hasle A HAS-OLS | 0
43 | 1 | 27 | b | CB | FALSE | Hasle B HAS-OLS | 0
44 | 0 | 28 | b | CB | TRUE | Hasle A2 | 0
45 | 1 | 28 | b | CB | FALSE | Hasle B2 | 0
46 | 0 | 29 | b | CB | TRUE | Hasle A3 | 0
47 | 1 | 29 | b | CB | FALSE | Hasle B3 | 0
48 | 2 | 4 | b | CB | TRUE | VÆR A VIA-VÆR | 0
49 | 2 | 26 | b | CB | TRUE | VÆR A VÆR-SYD | 0
50 | 2 | 32 | b | CB | TRUE | VÆR A SNO-VÆR | 0
51 | 3 | 32 | b | CB | FALSE | VÆR B Blok 6 | 0
52 | 3 | 4 | b | CB | FALSE | VÆR B VIA-VÆR | 0
53 | 3 | 26 | b | CB | FALSE | VÆR B VÆR-SYD | 0
54 | 17 | 19 | b | CB | TRUE | VIA A VIA-VÆR | 0
55 | 17 | 20 | b | CB | TRUE | VIA A VIA-SYD | 0
56 | 18 | 19 | b | CB | FALSE | VIA B2 | 0
57 | 18 | 20 | b | CB | FALSE | VIA B3 | 0
58 | 17 | 21 | b | CB | TRUE | VIA A NOR-VIA | 0
59 | 18 | 21 | b | CB | FALSE | VIA B1 | 0
60 | 2 | 24 | b | CB | TRUE | VÆR A VÆR-VES | 0
61 | 3 | 24 | b | CB | FALSE | VÆR B VES-VÆR | 0
62 | 2 | 25 | b | CB | TRUE | VÆR SwitchA Trf 1 Diesler | 0
63 | 3 | 31 | b | CB | FALSE | VÆR B7(1) | 0
64 | 34 | 2 | b | CB | TRUE | VÆR Trf Blok 6 | 0
65 | 2 | 31 | b | CB | TRUE | VÆR Tra Blok 5 | 0
66 | 3 | 34 | b | CB | FALSE | VÆR B Blok 5 | 0
67 | 3 | 25 | b | CB | FALSE | VÆR SwitchB Trf 1 Diesler | 0
68 | 2 | 30 | b | CB | TRUE | VÆR A-breaker Trf 2 Gl Dampværk | 0
69 | 3 | 30 | b | CB | FALSE | VÆR B-breaker Trf 2 Gl Dampværk | 0
70 | 17 | 35 | b | CB | TRUE | VIA A Trf | 0
71 | 18 | 35 | b | CB | FALSE | VIA B Trf | 0
72 | 39 | 37 | b | CB | TRUE | Gl Dampværk B afg 7(1) | 0
73 | 40 | 39 | b | CB | TRUE | Gl Dampværk A afg Load | 0
74 | 38 | 37 | b | CB | TRUE | Gl Dampværk B-breaker Trf2 MV | 0
75 | 40 | 38 | b | CB | TRUE | Gl Dampvært A Trf2 | 0
76 | 40 | 41 | b | CB | FALSE | Gl Dampværk B afg 7(3) | 0
77 | 41 | 37 | b | CB | FALSE | Gl Dampværk B afg 7(2) | 0
78 | 0 | 51 | b | CB | TRUE | Hasle A Trf1 | 0
79 | 1 | 51 | b | CB | FALSE | Hasle B Trf1 | 0
80 | 0 | 50 | b | CB | TRUE | Hasle A Trf2 | 0
81 | 1 | 50 | b | CB | FALSE | Hasle B Trf2 | 0
82 | 0 | 52 | b | CB | FALSE | Hasle A Trf2(1) | 0
83 | 1 | 52 | b | CB | FALSE | Hasle B Trf2(1) | 0
84 | 2 | 63 | b | CB | FALSE | VÆR A7 Tra 1 | 0
85 | 3 | 64 | b | CB | FALSE | VÆR B7 | 0
86 | 2 | 65 | b | CB | FALSE | VÆR A8 Trf 2 | 0
87 | 3 | 66 | b | CB | FALSE | VÆR B8 | 0
88 | 2 | 67 | b | CB | FALSE | VÆR A5 | 0
89 | 3 | 68 | b | CB | FALSE | VÆR B5 | 0
90 | 2 | 69 | b | CB | FALSE | VÆR A6 | 0
91 | 3 | 70 | b | CB | FALSE | VÆR B6 | 0
92 | 6 | 0 | l | CB | TRUE | Olsker\OLS-HAS\Switch OLS-HAS | 0
93 | 27 | 1 | l | CB | TRUE | Hasle C OLS\HAS-OLS\Switch HAS-OLS | 0
94 | 22 | 2 | l | CB | TRUE | Rønne Nord\Cub_5\Switch | 0
95 | 28 | 2 | l | CB | TRUE | Hasle C NOR\Cub_3\Switch HAS-NOR | 0
96 | 5 | 4 | l | CB | TRUE | Snorrebakken\SNO-HAS\Switch SNO-HAS | 0
97 | 33 | 5 | l | CB | TRUE | Hasle C SNO\Cub_3\Switch HAS-SNO | 0
98 | 6 | 6 | l | CB | TRUE | Olsker\Cub_2\Switch | 0
99 | 7 | 6 | l | CB | TRUE | Allinge\Cub_1\Switch | 0
100 | 6 | 7 | l | CB | TRUE | Olsker\OLS-ØST\Switch OLS-ØST | 0
101 | 8 | 7 | l | CB | TRUE | Østerlars\ØST-OLS\Switch ØST-OLS | 0
102 | 8 | 8 | l | CB | TRUE | Østerlars\Cub_2\Switch | 0
103 | 9 | 8 | l | CB | TRUE | Gudhjem\Cub_1\Switch | 0
104 | 8 | 9 | l | CB | TRUE | Østerlars\ØST-DAL\Switch ØST-DAL | 0
105 | 10 | 9 | l | CB | TRUE | Dalslunde\Cub_1\Switch DAL-ØST | 0
106 | 10 | 10 | l | CB | TRUE | Dalslunde\Cub_2\Switch DAL-SVA | 0
107 | 11 | 10 | l | CB | TRUE | Svaneke\SVA-DAL\Switch | 0
108 | 16 | 11 | l | CB | TRUE | Nexø\Cub_2\Switch | 0
109 | 12 | 11 | l | CB | TRUE | Bodilsker\Cub_1\Switch | 0
110 | 12 | 12 | l | CB | TRUE | Bodilsker\Cub_2\Switch | 0
111 | 13 | 12 | l | CB | TRUE | Poulsker\Cub_1\Switch | 0
112 | 12 | 13 | l | CB | TRUE | Bodilsker\BOD-ÅKI\Switch BOD-ÅKI | 0
113 | 14 | 13 | l | CB | TRUE | Åkirkeby\ÅKI-BOD\Switch ÅKI-BOD | 0
114 | 14 | 14 | l | CB | TRUE | Åkirkeby\ÅKI-SYD\Switch ÅKI-SYD | 0
115 | 15 | 14 | l | CB | TRUE | Rønne Syd\SYD-ÅKI\Switch SYD-ÅKI | 0
116 | 15 | 15 | l | CB | TRUE | Rønne Syd\Cub_3\Switch SYD-VIA | 0
117 | 22 | 16 | l | CB | TRUE | Rønne Nord\Cub_2\Switch | 0
118 | 12 | 17 | l | CB | TRUE | Bodilsker\BOD-DAL\Switch BOD-DAL | 0
119 | 10 | 17 | l | CB | TRUE | Dalslunde\Cub_3\Switch DAL-BOD | 0
120 | 11 | 18 | l | CB | TRUE | Svaneke\Cub_2\Switch | 0
121 | 16 | 18 | l | CB | TRUE | Nexø\Cub_3\Switch | 0
122 | 23 | 19 | l | CB | TRUE | Vesthavnen\Cub_1\Switch | 0
123 | 23 | 20 | l | CB | TRUE | Vesthavnen\Cub_2\Switch | 0
124 | 22 | 20 | l | CB | TRUE | Rønne Nord\Cub_3\Switch | 0
125 | 15 | 21 | l | CB | TRUE | Rønne Syd\Cub_8\Switch SYD-VÆR | 0
126 | 26 | 21 | l | CB | TRUE | Værket C SYD\Cub_4\Switch | 0
127 | 5 | 22 | l | CB | TRUE | Snorrebakken\Cub_4\Switch | 0
128 | 32 | 23 | l | CB | TRUE | Værket C SNO\Cub_4\Switch | 0
129 | 51 | 24 | l | CB | TRUE | Hasle C Trf 1\HAS 60kV TRF1\Switch | 0
130 | 49 | 25 | l | CB | TRUE | Hasle 10kV\HAS 10kV TRF1\Switch | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
0 | 29 | Reaktor 12 Mvar | 12 | 0 | 63 | 1 | 1 | TRUE
1 | 37 | Gl Dampværk FixReactor | 0.8 | 0 | 10.5 | 1 | 1 | TRUE
2 | 37 | Variabel (Fast) | 3.2 | 0 | 10.5 | 1 | 1 | TRUE
3 | 44 | BOD reactor | 2 | 0 | 10.5 | 1 | 1 | TRUE
4 | 55 | SYD reactor | 2 | 0 | 10.5 | 1 | 1 | TRUE
5 | 62 | SVA reactor | 2 | 0 | 10.5 | 1 | 1 | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max | r0x0_max | x0x_max | r0x0_min | x0x_min | description
0 | Sverige Slack | 29 | 1 | 0 | 1 | TRUE | 10000 | 8000 | 0.1 | 0.1 | 0.1 | 1 | 0.1 | 1

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km | alpha | temperature_degree_celsius | description | section | line_idx | folder_id | equipment | section_idx
0 | HAS-OLS | OHL 3x1x130StAl+50Fe | 6 | 71 | 6.818 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  | HAS-OLS(1) | 0 | Net 60kV |  | 0
1 | HAS-OLS | OHL 3x1x130StAl+50Fe Dobbelt | 71 | 27 | 4.589 | 0.286 | 0.4046 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5001 | 1.262 | 6.29 | 0.00403 | 90 |  | HAS-OLS | 0 | Net 60kV |  | 0
2 | HAS-NOR | PEX 3x1x240Al+35Cu | 22 | 28 | 7.434 | 0.139 | 0.133 | 170 | 0 | 0.425 | 1 | 1 | cs | TRUE | 0.591 | 0.209 | 170 | 0.00403 | 90 |  |  | 1 | Net 60kV |  | 0
3 | VIA-VÆR | PEX 3x1x300Al+35Cu | 4 | 19 | 1.481 | 0.111 | 0.129 | 180 | 0 | 0.48 | 1 | 1 | cs | TRUE | 0.566 | 0.205 | 180 | 0.00403 | 90 |  |  | 2 | Net 60kV |  | 0
4 | HAS-SNO | OHL 3x1x130StAl+50Fe | 5 | 72 | 5.217 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  | HAS-SNO(1) | 3 | Net 60kV |  | 0
5 | HAS-SNO | OHL 3x1x130StAl+50Fe Dobbelt | 72 | 33 | 4.588 | 0.286 | 0.4046 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5001 | 1.262 | 6.29 | 0.00403 | 90 |  | HAS-SNO | 3 | Net 60kV |  | 0
6 | ALL-OLS | PEX 3x1x150Al+25Cu | 6 | 7 | 4.276 | 0.228 | 0.146 | 140 | 0 | 0.325 | 1 | 1 | cs | TRUE | 0.809 | 0.328 | 140 | 0.00403 | 90 |  |  | 4 | Net 60kV |  | 0
7 | OLS-ØST | OHL 3x1x130StAl+50Fe | 6 | 8 | 13.05 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  |  | 5 | Net 60kV |  | 0
8 | GUD-ØST | PEX 3x1x150Al+25Cu | 8 | 9 | 6.6 | 0.228 | 0.146 | 140 | 0 | 0.325 | 1 | 1 | cs | TRUE | 0.809 | 0.328 | 140 | 0.00403 | 90 |  |  | 6 | Net 60kV |  | 0
9 | ØST-DAL | OHL 3x1x130StAl+50Fe | 8 | 10 | 9.924 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  |  | 7 | Net 60kV |  | 0
10 | SVA-DAL | PEX 3x1x150Al+25Cu | 10 | 11 | 7.531 | 0.228 | 0.146 | 140 | 0 | 0.325 | 1 | 1 | cs | TRUE | 0.809 | 0.328 | 140 | 0.00403 | 90 |  |  | 8 | Net 60kV |  | 0
11 | BOD-NEX | PEX 3x1x95Al+25Cu | 16 | 12 | 3.477 | 0.352 | 0.158 | 120 | 0 | 0.255 | 1 | 1 | cs | TRUE | 0.924 | 0.34 | 120 | 0.00403 | 90 |  |  | 9 | Net 60kV |  | 0
12 | BOD-POU | PEX 3x1x150Al+25Cu | 12 | 13 | 5.95 | 0.228 | 0.146 | 140 | 0 | 0.325 | 1 | 1 | cs | TRUE | 0.809 | 0.328 | 140 | 0.00403 | 90 |  |  | 10 | Net 60kV |  | 0
13 | ÅKI-BOD | OHL 3x1x130StAl+50Fe | 12 | 14 | 10.891 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  |  | 11 | Net 60kV |  | 0
14 | SYD-ÅKI | OHL 3x1x130StAl+50Fe | 14 | 15 | 10.995 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  |  | 12 | Net 60kV |  | 0
15 | VIA-SYD | PEX 3x1x240Al+35Cu | 15 | 20 | 1.674 | 0.139 | 0.133 | 170 | 0 | 0.425 | 1 | 1 | cs | TRUE | 0.591 | 0.209 | 170 | 0.00403 | 90 |  |  | 13 | Net 60kV |  | 0
16 | NOR-VIA | PEX 3x1x240Al+35Cu | 21 | 22 | 1.834 | 0.139 | 0.133 | 170 | 0 | 0.425 | 1 | 1 | cs | TRUE | 0.591 | 0.209 | 170 | 0.00403 | 90 |  |  | 14 | Net 60kV |  | 0
17 | DAL-BOD | OHL 3x1x130StAl+50Fe | 12 | 10 | 4.138 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  |  | 15 | Net 60kV |  | 0
18 | SVA-NEX | PEX 3x1x150Al+25Cu | 11 | 16 | 9.78 | 0.228 | 0.146 | 140 | 0 | 0.325 | 1 | 1 | cs | TRUE | 0.809 | 0.328 | 140 | 0.00403 | 90 |  |  | 16 | Net 60kV |  | 0
19 | VES-VÆR | PEX 3x1x300Al+35Cu | 24 | 23 | 1.8 | 0.111 | 0.129 | 180 | 0 | 0.48 | 1 | 1 | cs | TRUE | 0.566 | 0.205 | 180 | 0.00403 | 90 |  |  | 17 | Net 60kV |  | 0
20 | NOR-VES | PEX 3x1x300Al+35Cu | 23 | 22 | 2.2 | 0.111 | 0.129 | 180 | 0 | 0.48 | 1 | 1 | cs | TRUE | 0.566 | 0.205 | 180 | 0.00403 | 90 |  |  | 18 | Net 60kV |  | 0
21 | VÆR-SYD | APBF 1x3x95 Cu | 15 | 26 | 2.861 | 0.205 | 0.121 | 280 | 0 | 0.3 | 1 | 1 | cs | TRUE | 0.76 | 0.311 | 280 | 0.00403 | 90 |  |  | 19 | Net 60kV |  | 0
22 | SNO-VÆR | OHL 3x1x130StAl+50Fe | 5 | 73 | 0.698 | 0.286 | 0.4086 | 8.98 | 0 | 0.47 | 1 | 1 | ol | TRUE | 0.5045 | 1.252 | 6.29 | 0.00403 | 90 |  | SNO-VÆR | 20 | Net 60kV |  | 0
23 | SNO-VÆR | APBF 1x3x95 Cu | 73 | 32 | 3.453 | 0.205 | 0.121 | 280 | 0 | 0.3 | 1 | 1 | cs | TRUE | 0.76 | 0.311 | 280 | 0.00403 | 90 |  | SNO-VÆR(1) | 20 | Net 60kV |  | 0
24 | Line | 60kV 0 ohm line | 53 | 51 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | cs | FALSE | 0 | 0 | 0 | 0.00403 | 80 |  |  | 21 | 02 Hasle |  | 0
25 | HS TRF1 LV | 10kV 0 ohm line | 54 | 49 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | cs | FALSE | 0 | 0 | 0 | 0.00403 | 80 |  |  | 22 | 02 Hasle |  | 0

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_set_vm_pu | description | equipment
0 | Viadukten Trf | Trf 10 MVA ek 7.9 er 0.54 | 35 | 36 | 10 | 63 | 11 | 7.9 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
1 | Rønne Nord Trf | Trf 10 MVA ek 7.94 er 0.58 | 22 | 42 | 10 | 63 | 11 | 7.94 | 0.58 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
2 | Nexø Trf 1 | SEA 63/11 10 MVA NEXØ | 16 | 43 | 10 | 63 | 11 | 8.11 | 0.33077 | 0 | 0 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 3 | 0 | 100 | 0 | 0.9 | 1
3 | Nexø Trf 2 | Trf 10 MVA ek 8.4 er 0.61 | 16 | 43 | 10 | 63 | 11 | 8.4 | 0.61 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
4 | Bodilsker Trf 1 | Trf 10/12 MVA ek 8.87 er 0.54 | 12 | 44 | 12 | 63 | 11 | 8.87 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
5 | Povlsker Trf | Trf 10 MVA ek 8.14 er 0.59 | 13 | 45 | 10 | 63 | 11 | 8.14 | 0.59 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
6 | Åkirkeby Trf 22 | Trf 16 MVA ek 8.8 er 0.3 | 14 | 46 | 16 | 63 | 11 | 8.8 | 0.3 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
7 | Åkirkeby Trf 21 | Trf 25/31.5 MVA ek 10% | 14 | 46 | 25 | 63 | 11 | 10.02 | 0.308 | 9.5 | 0.1 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 2 | FALSE | 1 | 1 | TRUE | 10 | 0.308 | 100 | 0 | 0.9 | 1 | Mangler at få opdateret noget tomgangstab m.m.
8 | Snorrebakken Trf | Trf 10 MVA ek 8.5 er 0.62 | 5 | 47 | 10 | 63 | 11 | 8.5 | 0.62 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
9 | Vesthavn Trf | Trf 10 MVA ek 8.1 er 0.54 | 23 | 48 | 10 | 63 | 11 | 8.1 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
10 | Hasle Trf 2 | Trf 10 MVA ek 8.1 er 0.54 | 50 | 49 | 10 | 63 | 11 | 8.1 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
11 | HAS Trf1 | Trf 10 MVA ek 8.87 er 0.54 | 53 | 54 | 10 | 63 | 11 | 8.87 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 10 | FALSE | 1 | 1 | FALSE | 9 | 0 | 100 | 0 | 0.9 | 1
12 | Rønne Syd Trf | Trf 10 MVA ek 8.3 er 0.62 | 15 | 55 | 10 | 63 | 11 | 8.3 | 0.62 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
13 | Værket Trf 1 | Trf-1 16/20 MVA | 25 | 56 | 20 | 63 | 11 | 8.5 | 0.545 | 0 | 0.05 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 1 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
14 | Værket Trf 2 | Trf-2 25/31.5 MVA | 30 | 38 | 31.5 | 63 | 11 | 9 | 0.31121 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 1 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
15 | Olsker Trf 1 | Trf 4 MVA ek 7.4 er 0.3 | 6 | 58 | 4 | 60 | 10 | 7.4 | 0.3 | 0 | 0.5 | 330 | hv | 10 | 1 | 19 | 1.7 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
16 | Olsker Trf 2 | Trf 4 MVA ek 7.4 er 0.3 | 6 | 58 | 4 | 60 | 10 | 7.4 | 0.3 | 0 | 0.5 | 330 | hv | 10 | 1 | 19 | 1.7 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
17 | Allinge Trf 1 | Trf 10 MVA ek 8.4 er 0.61 | 7 | 59 | 10 | 63 | 11 | 8.4 | 0.61 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
18 | Allinge Trf 2 | Trf 10 MVA ek 8.04 er 0.53 | 7 | 59 | 10 | 63 | 11 | 8.04 | 0.53 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
19 | Østerlars Trf | Trf 6.3 MVA ek8.5 er0.7 | 8 | 60 | 6.3 | 63 | 11 | 8.5 | 0.7 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
20 | Gudhjem Trf | Trf 4 MVA ek 7.3 er 0.3 N.2 | 9 | 61 | 4 | 60 | 10 | 7.2 | 0.3 | 0 | 0.5 | 330 | hv | 10 | 1 | 19 | 1.7 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1
21 | Svaneke Trf | Trf 10 MVA ek 8.3 er 0.54 | 11 | 62 | 10 | 63 | 11 | 8.3 | 0.54 | 0 | 0.5 | 330 | hv | 8 | 1 | 15 | 2 | 0 | 3 | FALSE | 1 | 1 | TRUE | 9 | 0 | 100 | 0 | 0.9 | 1

## controller
| object | in_service | order | level | initial_run | recycle
0 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 0}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 0}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 0}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 36}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 0}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 36}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
1 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 1}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 1}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 1}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 42}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 1}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 42}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
2 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 2}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 2}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 2}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 43}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 2}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 43}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
3 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 3}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 3}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 3}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 43}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 3}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 43}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
4 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 4}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 4}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 4}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 44}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 4}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 44}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
5 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 5}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 5}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 5}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 45}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 5}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 45}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
6 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 6}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 6}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 6}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 46}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 6}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 46}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
7 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 7}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 7}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 7}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 46}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 7}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 46}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 2}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
8 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 8}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 8}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 8}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 47}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 8}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 47}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
9 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 9}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 9}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 9}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 48}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 9}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 48}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
10 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 10}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 10}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 10}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 49}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 10}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 49}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
11 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 11}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 11}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 11}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 54}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 11}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 54}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 10}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
12 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 12}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 12}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 12}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 55}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 12}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 55}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
13 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 13}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 13}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 13}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 56}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 13}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 56}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
14 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 14}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 14}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 14}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 38}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 14}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 38}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
15 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 15}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 15}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 15}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 58}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 15}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 58}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 19}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 10}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.7000000476837158}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.009500000238418578}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
16 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 16}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 16}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 16}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 58}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 16}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 58}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 19}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 10}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.7000000476837158}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.009500000238418578}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
17 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 17}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 17}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 17}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 59}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 17}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 59}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
18 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 18}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 18}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 18}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 59}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 18}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 59}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
19 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 19}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 19}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 19}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 60}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 19}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 60}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
20 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 20}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 20}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 20}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 61}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 20}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 61}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 19}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 10}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.7000000476837158}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.009500000238418578}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}
21 | { "_module": "pandapower.control.controller.trafo.DiscreteTapControl", "_class": "DiscreteTapControl", "_object": "{\"index\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 21}, \"matching_params\": {\"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 21}, \"trafotype\": \"2W\"}, \"trafotype\": \"2W\", \"tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 21}, \"trafotable\": \"trafo\", \"side\": \"lv\", \"_read_write_flag\": \"single_index\", \"trafobus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 62}, \"controlled_tid\": {\"_module\": \"numpy\", \"_class\": \"int64\", \"_object\": 21}, \"controlled_bus\": {\"_module\": \"numpy\", \"_class\": \"uint32\", \"_object\": 62}, \"tap_min\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 1}, \"tap_max\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 15}, \"tap_neutral\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 8}, \"tap_step_percent\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 2.0}, \"tap_step_degree\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.0}, \"tap_pos\": {\"_module\": \"numpy\", \"_class\": \"int32\", \"_object\": 3}, \"tap_sign\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 1.0}, \"tap_side_coeff\": 1, \"tol\": 0.001, \"vm_lower_pu\": 0.9879999756813049, \"vm_upper_pu\": 1.0119999647140503, \"vm_delta_pu\": {\"_module\": \"numpy\", \"_class\": \"float64\", \"_object\": 0.011}, \"_vm_set_pu\": null}" } | TRUE | 0 | 0 | TRUE | {"trafo": true, "gen": false, "bus_pq": false}

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating | endtemp_degree | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
PEX 3x1x95Al+25Cu | 120 | 0.352 | 0.158 | 0.255 | cs | 0 | 0.00403 |  | 120 | 0.924 | 0.34 | 120
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
PEX 3x1x240Al+35Cu | 170 | 0.139 | 0.133 | 0.425 | cs | 0 | 0.00403 |  | 120 | 0.591 | 0.209 | 170
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
10kV 0 ohm line | 0 | 0 | 0 | 2 | cs | 0 | 0.00403 |  | 80 | 0 | 0 | 0
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
OHL 3x1x130StAl+50Fe | 8.98 | 0.286 | 0.4086 | 0.47 | ol | 0 | 0.00403 |  | 120 | 0.5045 | 1.252 | 6.29
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
OHL 3x1x130StAl+50Fe Dobbelt | 8.98 | 0.286 | 0.4046 | 0.47 | ol | 0 | 0.00403 |  | 120 | 0.5001 | 1.262 | 6.29
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
APBF 1x3x95 Cu | 280 | 0.205 | 0.121 | 0.3 | cs | 0 | 0.00403 |  | 120 | 0.76 | 0.311 | 280
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
PEX 3x1x300Al+35Cu | 180 | 0.111 | 0.129 | 0.48 | cs | 0 | 0.00403 |  | 120 | 0.566 | 0.205 | 180
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
PEX 3x1x150Al+25Cu | 140 | 0.228 | 0.146 | 0.325 | cs | 0 | 0.00403 |  | 120 | 0.809 | 0.328 | 140
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
60kV 0 ohm line | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 |  | 80 | 0 | 0 | 0

## trafo_std_types
| sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | vector_group | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_side | tap_step_percent | tap_step_degree | tap_phase_shifter | tap_max | tap_min | tap_neutral
Trf 10 MVA ek 7.9 er 0.54 | 10 | 63 | 11 | 7.9 | 0.54 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 10/12 MVA ek 8.87 er 0.54 | 12 | 63 | 11 | 8.87 | 0.54 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
40 MVA 110/10 kV | 40 | 110 | 10 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
160 MVA 380/110 kV | 160 | 380 | 110 | 12.2 | 0.25 | 60 | 0.06 | 0 | Yy0 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
Trf 10 MVA ek 8.3 er 0.62 | 10 | 63 | 11 | 8.3 | 0.62 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 10 MVA ek 8.87 er 0.54 | 10 | 63 | 11 | 8.87 | 0.54 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
63 MVA 110/20 kV | 63 | 110 | 20 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
0.25 MVA 20/0.4 kV | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | Yzn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
0.63 MVA 20/0.4 kV | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | Dyn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
Trf 10 MVA ek 8.1 er 0.54 | 10 | 63 | 11 | 8.1 | 0.54 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 4 MVA ek 7.4 er 0.3 | 4 | 60 | 10 | 7.4 | 0.3 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 1.7 | 0 | FALSE | 19 | 1 | 10
Trf 4 MVA ek 7.3 er 0.3 N.2 | 4 | 60 | 10 | 7.2 | 0.3 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 1.7 | 0 | FALSE | 19 | 1 | 10
100 MVA 220/110 kV | 100 | 220 | 110 | 12 | 0.26 | 55 | 0.06 | 0 | Yy0 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
0.25 MVA 10/0.4 kV | 0.25 | 10 | 0.4 | 4 | 1.2 | 0.6 | 0.24 | 150 | Dyn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
SEA 63/11 10 MVA NEXØ | 10 | 63 | 11 | 8.11 | 0.33077 | 0 | 0 | 330 | YNd1 | 3 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 10 MVA ek 7.94 er 0.58 | 10 | 63 | 11 | 7.94 | 0.58 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
25 MVA 110/20 kV | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
40 MVA 110/20 kV | 40 | 110 | 20 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
Trf 6.3 MVA ek8.5 er0.7 | 6.3 | 63 | 11 | 8.5 | 0.7 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 10 MVA ek 8.5 er 0.62 | 10 | 63 | 11 | 8.5 | 0.62 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 10 MVA ek 8.3 er 0.54 | 10 | 63 | 11 | 8.3 | 0.54 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf-2 25/31.5 MVA | 31.5 | 63 | 11 | 9 | 0.31121 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
0.4 MVA 20/0.4 kV | 0.4 | 20 | 0.4 | 6 | 1.425 | 1.35 | 0.3375 | 150 | Dyn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
Trf 10 MVA ek 8.14 er 0.59 | 10 | 63 | 11 | 8.14 | 0.59 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
0.4 MVA 10/0.4 kV | 0.4 | 10 | 0.4 | 4 | 1.325 | 0.95 | 0.2375 | 150 | Dyn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
Trf 10 MVA ek 8.4 er 0.61 | 10 | 63 | 11 | 8.4 | 0.61 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
0.63 MVA 10/0.4 kV | 0.63 | 10 | 0.4 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | Dyn5 | [5 empty] | hv | 2.5 | 0 | FALSE | 2 | -2 | 0
Trf 10 MVA ek 8.04 er 0.53 | 10 | 63 | 11 | 8.04 | 0.53 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 25/31.5 MVA ek 10% | 25 | 63 | 11 | 10.02 | 0.308 | 9.5 | 0.1 | 330 | YNd1 | 10 | 0.308 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
Trf 16 MVA ek 8.8 er 0.3 | 16 | 63 | 11 | 8.8 | 0.3 | 0 | 0.5 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8
25 MVA 110/10 kV | 25 | 110 | 10 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
63 MVA 110/10 kV | 63 | 110 | 10 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 1.5 | 0 | FALSE | 9 | -9 | 0
Trf-1 16/20 MVA | 20 | 63 | 11 | 8.5 | 0.545 | 0 | 0.05 | 330 | YNd1 | 9 | 0 | 100 | 0 | 0.9 | hv | 2 | 0 | FALSE | 15 | 1 | 8

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar | pf_vm_pu | pf_va_degree
0 |  |  |  |  | 1 | 0.10704
1 |  |  |  |  | 0 | 0
2 |  |  |  |  | 0.99775 | 5.3086e-30
3 |  |  |  |  | 0 | 0
4 |  |  |  |  | 0.99775 | -4.5563e-11
5 |  |  |  |  | 0.99817 | 0.0013071
6 |  |  |  |  | 0.9995 | -0.26637
7 |  |  |  |  | 0.9994 | -0.28167
8 |  |  |  |  | 0.99838 | -0.5111
9 |  |  |  |  | 0.99832 | -0.5346
10 |  |  |  |  | 0.99714 | -0.54756
11 |  |  |  |  | 0.99658 | -0.55087
12 |  |  |  |  | 0.99682 | -0.53468
13 |  |  |  |  | 0.9969 | -0.55974
14 |  |  |  |  | 0.99694 | -0.34198
15 |  |  |  |  | 0.99759 | -0.013107
16 |  |  |  |  | 0.99661 | -0.5571
17 |  |  |  |  | 0.99778 | -0.0019601
18 |  |  |  |  | 0 | 0
19 |  |  |  |  | 0.99778 | -0.0019601
20 |  |  |  |  | 0.99778 | -0.0019601
21 |  |  |  |  | 0.99778 | -0.0019601
22 |  |  |  |  | 0.99807 | 0.010631
23 |  |  |  |  | 0.9979 | 0.0033156
24 |  |  |  |  | 0.99775 | -6.851e-11
25 |  |  |  |  | 0.99775 | 5.3e-13
26 |  |  |  |  | 0.99775 | -6.6663e-11
27 |  |  |  |  | 1 | 0.10704
28 |  |  |  |  | 1 | 0.10704
29 |  |  |  |  | 1 | 0.10704
30 |  |  |  |  | 0.99775 | 2.6255e-10
31 |  |  |  |  | 0.99775 | 5.3086e-30
32 |  |  |  |  | 0.99775 | -8.2345e-11
33 |  |  |  |  | 1 | 0.10704
34 |  |  |  |  | 0.99775 | 5.3086e-30
35 |  |  |  |  | 0.99778 | -0.0019601
36 |  |  |  |  | 1.0001 | 29.5569
37 |  |  |  |  | 1.0109 | 29.789
38 |  |  |  |  | 1.0109 | 29.789
39 |  |  |  |  | 1.0109 | 29.789
40 |  |  |  |  | 1.0109 | 29.789
41 |  |  |  |  | 0 | 0
42 |  |  |  |  | 0.99953 | 29.6033
43 |  |  |  |  | 1.0022 | 28.8993
44 |  |  |  |  | 1.0072 | 29.243
45 |  |  |  |  | 1.0085 | 29.2169
46 |  |  |  |  | 1.0065 | 29.257
47 |  |  |  |  | 1.0034 | 29.5406
48 |  |  |  |  | 1.0062 | 29.8396
49 |  |  |  |  | 1.0105 | 29.7732
50 |  |  |  |  | 1 | 0.10704
51 |  |  |  |  | 1 | 0.10704
52 |  |  |  |  | 0 | 0
53 |  |  |  |  | 0 | 0
54 |  |  |  |  | 0 | 0
55 |  |  |  |  | 1.0072 | 29.4874
56 |  |  |  |  | 1.005 | 30.0001
57 |  |  |  |  | 0 | 0
58 |  |  |  |  | 1.0047 | 29.132
59 |  |  |  |  | 1.0084 | 29.3043
60 |  |  |  |  | 1.0059 | 28.7116
61 |  |  |  |  | 0.99997 | 28.891
62 |  |  |  |  | 1.0041 | 29.0502

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent | pf_loading
0 | [14 empty] | 8.9762
1 | [14 empty] | 8.9762
2 | [14 empty] | 15.4991
3 | [14 empty] | 1.5489
4 | [14 empty] | 4.1386
5 | [14 empty] | 4.1386
6 | [14 empty] | 3.4891
7 | [14 empty] | 5.2958
8 | [14 empty] | 3.9592
9 | [14 empty] | 2.2302
10 | [14 empty] | 4.2625
11 | [14 empty] | 5.3188
12 | [14 empty] | 4.4719
13 | [14 empty] | 4.845
14 | [14 empty] | 8.1884
15 | [14 empty] | 7.1739
16 | [14 empty] | 8.906
17 | [14 empty] | 1.5287
18 | [14 empty] | 2.8531
19 | [14 empty] | 4.1871
20 | [14 empty] | 4.3213
21 | [14 empty] | 5.7796
22 | [14 empty] | 5.7084
23 | [14 empty] | 5.7084
24 | [14 empty] | 0
25 | [14 empty] | 0

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent | pf_loading
0 | [13 empty] | 10.9432
1 | [13 empty] | 10.924
2 | [13 empty] | 11.3689
3 | [13 empty] | 0
4 | [13 empty] | 18.2661
5 | [13 empty] | 7.0614
6 | [13 empty] | 0
7 | [13 empty] | 7.0321
8 | [13 empty] | 9.3166
9 | [13 empty] | 3.6694
10 | [13 empty] | 8.0424
11 | [13 empty] | 0
12 | [13 empty] | 22.2265
13 | [13 empty] | 0.046122
14 | [13 empty] | 15.1571
15 | [13 empty] | 16.8155
16 | [13 empty] | 0
17 | [13 empty] | 8.5617
18 | [13 empty] | 0
19 | [13 empty] | 15.3485
20 | [13 empty] | 14.8711
21 | [13 empty] | 23.5469

## res_ext_grid
| p_mw | q_mvar | pf_p | pf_q
0 |  |  | 13.7609 | 9.0836

## res_load
| p_mw | q_mvar | pf_p | pf_q
0 |  |  | 0 | 0
1 |  |  | 0 | 0
2 |  |  | 0.929 | 0.478
3 |  |  | 1.37 | 0.26
4 |  |  | 0.866 | 0.58
5 |  |  | 1.079 | 0.137
6 |  |  | 0.618 | -0.026
7 |  |  | 0.405 | -0.546
8 |  |  | 1.587 | -0.578
9 |  |  | 0.883 | 0.129
10 |  |  | 0.317 | -0.154
11 |  |  | 0.641 | -0.437
12 |  |  | 1.128 | -0.214
13 |  |  | 0 | 0
14 |  |  | 0.615 | -0.354
15 |  |  | 0.78 | -0.266
16 |  |  | 0.922 | -0.109
17 |  |  | 0.608 | -0.143
18 |  |  | 0.923 | 0.043

## res_shunt
| p_mw | q_mvar | vm_pu | pf_p | pf_q
0 |  |  |  | -1.2e-14 | 12
1 |  |  |  | 0 | 0.81752
2 |  |  |  | 0 | 3.2701
3 |  |  |  | 0 | 2.0288
4 |  |  |  | 0 | 2.029
5 |  |  |  | 0 | 2.0166

## res_switch
| i_ka | loading_percent | pf_closed | pf_in_service
0 |  |  | TRUE | TRUE
1 |  |  | TRUE | TRUE
2 |  |  | TRUE | TRUE
3 |  |  | TRUE | TRUE
4 |  |  | TRUE | TRUE
5 |  |  | FALSE | TRUE
6 |  |  | FALSE | TRUE
7 |  |  | TRUE | TRUE
8 |  |  | TRUE | TRUE
9 |  |  | TRUE | TRUE
10 |  |  | TRUE | TRUE
11 |  |  | FALSE | TRUE
12 |  |  | FALSE | TRUE
13 |  |  | TRUE | TRUE
14 |  |  | TRUE | TRUE
15 |  |  | TRUE | TRUE
16 |  |  | TRUE | TRUE
17 |  |  | TRUE | TRUE
18 |  |  | TRUE | TRUE
19 |  |  | TRUE | TRUE
20 |  |  | TRUE | TRUE
21 |  |  | TRUE | TRUE
22 |  |  | TRUE | TRUE
23 |  |  | TRUE | TRUE
24 |  |  | TRUE | TRUE
25 |  |  | TRUE | TRUE
26 |  |  | TRUE | TRUE
27 |  |  | TRUE | TRUE
28 |  |  | FALSE | TRUE
29 |  |  | FALSE | TRUE
30 |  |  | TRUE | TRUE
31 |  |  | TRUE | TRUE
32 |  |  | FALSE | TRUE
33 |  |  | FALSE | TRUE
34 |  |  | TRUE | TRUE
35 |  |  | TRUE | TRUE
36 |  |  | TRUE | TRUE
37 |  |  | TRUE | TRUE
38 |  |  | TRUE | TRUE
39 |  |  | TRUE | TRUE
40 |  |  | TRUE | TRUE
41 |  |  | FALSE | TRUE
42 |  |  | TRUE | TRUE
43 |  |  | FALSE | TRUE
44 |  |  | TRUE | TRUE
45 |  |  | FALSE | TRUE
46 |  |  | TRUE | TRUE
47 |  |  | FALSE | TRUE
48 |  |  | TRUE | TRUE
49 |  |  | TRUE | TRUE
50 |  |  | TRUE | TRUE
51 |  |  | FALSE | TRUE
52 |  |  | FALSE | TRUE
53 |  |  | FALSE | TRUE
54 |  |  | TRUE | TRUE
55 |  |  | TRUE | TRUE
56 |  |  | FALSE | TRUE
57 |  |  | FALSE | TRUE
58 |  |  | TRUE | TRUE
59 |  |  | FALSE | TRUE
60 |  |  | TRUE | TRUE
61 |  |  | FALSE | TRUE
62 |  |  | TRUE | TRUE
63 |  |  | FALSE | TRUE
64 |  |  | TRUE | TRUE
65 |  |  | TRUE | TRUE
66 |  |  | FALSE | TRUE
67 |  |  | FALSE | TRUE
68 |  |  | TRUE | TRUE
69 |  |  | FALSE | TRUE
70 |  |  | TRUE | TRUE
71 |  |  | FALSE | TRUE
72 |  |  | TRUE | TRUE
73 |  |  | TRUE | TRUE
74 |  |  | TRUE | TRUE
75 |  |  | TRUE | TRUE
76 |  |  | FALSE | TRUE
77 |  |  | FALSE | TRUE
78 |  |  | TRUE | TRUE
79 |  |  | FALSE | TRUE
80 |  |  | TRUE | TRUE
81 |  |  | FALSE | TRUE
82 |  |  | FALSE | TRUE
83 |  |  | FALSE | TRUE
84 |  |  | FALSE | TRUE
85 |  |  | FALSE | TRUE
86 |  |  | FALSE | TRUE
87 |  |  | FALSE | TRUE
88 |  |  | FALSE | TRUE
89 |  |  | FALSE | TRUE
90 |  |  | FALSE | TRUE
91 |  |  | FALSE | TRUE
92 |  |  | TRUE | TRUE
93 |  |  | TRUE | TRUE
94 |  |  | TRUE | TRUE
95 |  |  | TRUE | TRUE
96 |  |  | TRUE | TRUE
97 |  |  | TRUE | TRUE
98 |  |  | TRUE | TRUE
99 |  |  | TRUE | TRUE
100 |  |  | TRUE | TRUE
101 |  |  | TRUE | TRUE
102 |  |  | TRUE | TRUE
103 |  |  | TRUE | TRUE
104 |  |  | TRUE | TRUE
105 |  |  | TRUE | TRUE
106 |  |  | TRUE | TRUE
107 |  |  | TRUE | TRUE
108 |  |  | TRUE | TRUE
109 |  |  | TRUE | TRUE
110 |  |  | TRUE | TRUE
111 |  |  | TRUE | TRUE
112 |  |  | TRUE | TRUE
113 |  |  | TRUE | TRUE
114 |  |  | TRUE | TRUE
115 |  |  | TRUE | TRUE
116 |  |  | TRUE | TRUE
117 |  |  | TRUE | TRUE
118 |  |  | TRUE | TRUE
119 |  |  | TRUE | TRUE
120 |  |  | TRUE | TRUE
121 |  |  | TRUE | TRUE
122 |  |  | TRUE | TRUE
123 |  |  | TRUE | TRUE
124 |  |  | TRUE | TRUE
125 |  |  | TRUE | TRUE
126 |  |  | TRUE | TRUE
127 |  |  | TRUE | TRUE
128 |  |  | TRUE | TRUE
129 |  |  | FALSE | TRUE
130 |  |  | FALSE | TRUE

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | description | object
6 | bus | substat | object
7 | bus | folder_id | object
8 | bus | equipment | object
9 | load | name | object
10 | load | bus | uint32
11 | load | p_mw | float64
12 | load | q_mvar | float64
13 | load | const_z_percent | float64
14 | load | const_i_percent | float64
15 | load | sn_mva | float64
16 | load | scaling | float64
17 | load | in_service | bool
18 | load | type | object
19 | load | description | object
20 | load | equipment | object
21 | switch | bus | int64
22 | switch | element | int64
23 | switch | et | object
24 | switch | type | object
25 | switch | closed | bool
26 | switch | name | object
27 | switch | z_ohm | float64
28 | switch | in_ka | float64
29 | shunt | bus | uint32
30 | shunt | name | object
31 | shunt | q_mvar | float64
32 | shunt | p_mw | float64
33 | shunt | vn_kv | float64
34 | shunt | step | uint32
35 | shunt | max_step | uint32
36 | shunt | in_service | bool
37 | ext_grid | name | object
38 | ext_grid | bus | uint32
39 | ext_grid | vm_pu | float64
40 | ext_grid | va_degree | float64
41 | ext_grid | slack_weight | float64
42 | ext_grid | in_service | bool
43 | ext_grid | s_sc_max_mva | float64
44 | ext_grid | s_sc_min_mva | float64
45 | ext_grid | rx_min | float64
46 | ext_grid | rx_max | float64
47 | ext_grid | r0x0_max | float64
48 | ext_grid | x0x_max | float64
49 | ext_grid | r0x0_min | float64
50 | ext_grid | x0x_min | float64
51 | ext_grid | description | object
52 | line | name | object
53 | line | std_type | object
54 | line | from_bus | uint32
55 | line | to_bus | uint32
56 | line | length_km | float64
57 | line | r_ohm_per_km | float64
58 | line | x_ohm_per_km | float64
59 | line | c_nf_per_km | float64
60 | line | g_us_per_km | float64
61 | line | max_i_ka | float64
62 | line | df | float64
63 | line | parallel | uint32
64 | line | type | object
65 | line | in_service | bool
66 | line | r0_ohm_per_km | float64
67 | line | x0_ohm_per_km | float64
68 | line | c0_nf_per_km | float64
69 | line | alpha | float64
70 | line | temperature_degree_celsius | float64
71 | line | description | object
72 | line | section | object
73 | line | line_idx | float64
74 | line | folder_id | object
75 | line | equipment | object
76 | line | section_idx | int64
77 | trafo | name | object
78 | trafo | std_type | object
79 | trafo | hv_bus | uint32
80 | trafo | lv_bus | uint32
81 | trafo | sn_mva | float64
82 | trafo | vn_hv_kv | float64
83 | trafo | vn_lv_kv | float64
84 | trafo | vk_percent | float64
85 | trafo | vkr_percent | float64
86 | trafo | pfe_kw | float64
87 | trafo | i0_percent | float64
88 | trafo | shift_degree | float64
89 | trafo | tap_side | object
90 | trafo | tap_neutral | int32
91 | trafo | tap_min | int32
92 | trafo | tap_max | int32
93 | trafo | tap_step_percent | float64
94 | trafo | tap_step_degree | float64
95 | trafo | tap_pos | int32
96 | trafo | tap_phase_shifter | bool
97 | trafo | parallel | uint32
98 | trafo | df | float64
99 | trafo | in_service | bool
100 | trafo | vk0_percent | float64
101 | trafo | vkr0_percent | float64
102 | trafo | mag0_percent | float64
103 | trafo | mag0_rx | float64
104 | trafo | si0_hv_partial | float64
105 | trafo | tap_set_vm_pu | float64
106 | trafo | description | object
107 | trafo | equipment | object
108 | controller | object | object
109 | controller | in_service | bool
110 | controller | order | float64
111 | controller | level | object
112 | controller | initial_run | bool
113 | controller | recycle | object
114 | res_bus | vm_pu | float64
115 | res_bus | va_degree | float64
116 | res_bus | p_mw | float64
117 | res_bus | q_mvar | float64
118 | res_bus | pf_vm_pu | float64
119 | res_bus | pf_va_degree | float64
120 | res_line | p_from_mw | float64
121 | res_line | q_from_mvar | float64
122 | res_line | p_to_mw | float64
123 | res_line | q_to_mvar | float64
124 | res_line | pl_mw | float64
125 | res_line | ql_mvar | float64
126 | res_line | i_from_ka | float64
127 | res_line | i_to_ka | float64
128 | res_line | i_ka | float64
129 | res_line | vm_from_pu | float64
130 | res_line | va_from_degree | float64
131 | res_line | vm_to_pu | float64
132 | res_line | va_to_degree | float64
133 | res_line | loading_percent | float64
134 | res_line | pf_loading | float64
135 | res_trafo | p_hv_mw | float64
136 | res_trafo | q_hv_mvar | float64
137 | res_trafo | p_lv_mw | float64
138 | res_trafo | q_lv_mvar | float64
139 | res_trafo | pl_mw | float64
140 | res_trafo | ql_mvar | float64
141 | res_trafo | i_hv_ka | float64
142 | res_trafo | i_lv_ka | float64
143 | res_trafo | vm_hv_pu | float64
144 | res_trafo | va_hv_degree | float64
145 | res_trafo | vm_lv_pu | float64
146 | res_trafo | va_lv_degree | float64
147 | res_trafo | loading_percent | float64
148 | res_trafo | pf_loading | float64
149 | res_ext_grid | p_mw | float64
150 | res_ext_grid | q_mvar | float64
151 | res_ext_grid | pf_p | float64
152 | res_ext_grid | pf_q | float64
153 | res_load | p_mw | float64
154 | res_load | q_mvar | float64
155 | res_load | pf_p | float64
156 | res_load | pf_q | float64
157 | res_shunt | p_mw | float64
158 | res_shunt | q_mvar | float64
159 | res_shunt | vm_pu | float64
160 | res_shunt | pf_p | float64
161 | res_shunt | pf_q | float64
162 | res_switch | i_ka | float64
163 | res_switch | loading_percent | float64
164 | res_switch | pf_closed | object
165 | res_switch | pf_in_service | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva | pf_converged
0 | 2.14.10 | 2.14.0 | FALSE | FALSE | Summary Grid | 50 | 100 | TRUE